## Form 410-1 IP Units
CALCULATION PROCEDURE TO DETERMINE FIN EFFICIENCIES AND METAL THERMAL RESISTANCES (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [5 empty] | Date
Item No. | Item Abbreviation | General Description |  |  | Calculation Procedure | Dimensions | Numerical Input and Formulas
1 | - | Fin Type and Thickness Profile |  |  |  | --
| - | Fin Type |  |  | Choose | -- | --
| - | Fin Collar Type |  |  | Choose | -- | --
2 | As | Secondary Surface Area (See Appendix D, AHRI Std 410) |  |  |  | ft2
3 | Ap | Primary Surface Area (See Appendix D, AHRI Std 410) |  |  |  | ft2
4 | Ao | Total External Coil Surface |  |  | Area = (As + Ap) | ft2 | 0
5 | Di | Tube Inside Diameter |  |  |  | in
6 | Nt | Total Number of Tubes in Coil |  |  |  | --
7 | Lt | Finned Tube Length |  |  |  | in
8 | Ai | Total Internal Coil Surface Area |  |  | Area = (π·Di*Nt*Lt)/144 | ft2 | 0
9 | B | Surface Ratio |  |  | Ratio = (Ao/Ai) | -- | 0
10 | Df | Spiral Fin Outside Diameter |  |  |  | in
11* | Lf | Fin Length Perpendicular to Direction of Tubes * For non-circular shaped fins only |  |  |  | in
12* | Ld | Fin Depth in Direction of Air Flow * For non-circular shaped fins only |  |  |  | in
13 | Xe | Outside Radius of Equiv. Annular Area of Non-Circular, Annular or Spiral Fin |  |  |  | --
|  |  | Select Fin Type Above |  |  | in | 0
|  |  | - For Continuous Plate Fin |  | Xe = sqrt((Lf*Ld)/(π*Nt)) | in | 0
|  |  | - For Individually-Finned Tube |  | Xe = sqrt((Lf*Ld)/(π)) | in | 0
|  |  | - For Spiral Fin (Smooth and Crimped) |  | Xe = Df/2 | in | 0
14 | Do | Tube Outside Diameter |  |  |  | in
15 | Yf | Fin Thickness for Fin of Uniform Thickness |  |  |  | in
16 | Xb | Fin Root Radius
|  | Select Fin Collar Type Above |  |  |  | in | 0
|  | - for Plate Type Fins w/ Collars Not Touching Adjacent Fins |  |  | Xb = (Do + Yf)/2 | in | 0
|  | - for Plate Type Fins w/ Collars Touching Adjacent Fins |  |  | Xb = (Do + 2*Yf)/2 | in | 0
|  | - for Plate Type Fins w/o Collars or Spiral Fins |  |  | Xb = (Do)/2 | in | 0
17 | w | Height of Equivalent Actual Annular Fin |  |  | w = Xe - Xb | in | 0
18 | Xe/Xb | Radius Ratio of Equivalent Annular Fin |  |  | Xe/Xb = Xe/Xb | -- | 0
19 | kf | Fin Material Thermal Conductivity |  |  | See table 5 | Btu·ft/ h·ft2·°F
20 | kt | Tube Material Thermal Conductivity |  |  | See table 5 | Btu·ft/ h·ft2·°F
21 | Yr | Fin Thickness at Root of Spiral Fins |  |  |  | in
[7 empty] | value1 | value 2 | value 3 | value 4 | value 5
22 | fa | Air-Side Film Heat Transfer Coefficient Note: Arbitrarily assume various values, covering application ratings -suggested range 4 - 64 |  |  | For Dry Surface faD = 1/RaD For Wet Surface faW = 1/RaW* (m"/cp) | Btu/ h·ft2·°F | 4 | 8 | 16 | 32 | 64
23 | RaD | Air Film Thermal Resistance for Dry Surface |  |  | RaD = 1/fa | h·ft2·°F /Btu | 0.25 | 0.125 | 0.0625 | 0.03125 | 0.015625
24 |  | Fin Efficiency Parameter |  | err | err | -- | 0 | 0 | 0 | 0 | 0
24 |  | Fin Efficiency Parameter |  | - For Plate Type Fins | IP = w*sqrt(fa/(6*kf*Yf)) | -- | 0 | 0 | 0 | 0 | 0
|  |  |  | - For Spiral Fins | IP = w*sqrt(fa/(6*kf*Yr)) | -- | 0 | 0 | 0 | 0 | 0
25 | ϕ | Mean Fin Efficiency See fig. 29 and 32 |  |  |  | --
26 | η | Total Surface Effectiveness |  |  | η = ((ϕ*As) + Ap)/Ao | -- | 0 | 0 | 0 | 0 | 0
27 | Rf | Thermal Resistance of Fin Based on Total Surface Effectiveness |  |  | Rf = [(1-η)/η)](1/fa) | h·ft2·°F /Btu | 0 | 0 | 0 | 0 | 0
28 | Rt | Thermal Resistance of Tube |  |  | IP = ((B*Di)/(24*kt))*ln(Do/Di) | h·ft2·°F /Btu | 0 | 0 | 0 | 0 | 0
29 | RmD | Total Metal Resistance of Fin and Tube |  |  | RmD = Rf + Rt | h·ft2·°F /Btu | 0 | 0 | 0 | 0 | 0
30 |  | Combined Air Film plus Metal Thermal Resistance for Dry Surface Coil |  |  | RaD+RmD | h·ft2·°F /Btu | 0 | 0 | 0 | 0 | 0
31 |  | Plot (RaD+RmD) vs. RaD on rectilinear coordinates as shown in Fig. 13 |  |  |  | --
32 |  | Plot RmD vs. fa on rectilinear coordinates as shown in Fig. 14 |  |  |  | --