## Form 410-3 IP Units
CALCULATION OF TUBE-SIDE PRESSURE DROPS FROM STEAM AND WATER COIL TESTS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [6 empty] | Date
Solution Procedure Steps for Specific Coil Application |  | Coil Line: |  |  |  | Coil Type:
Coil Surface:
GENERAL PROCEDURE
Steam Coils | Water Coils | General Category | Item No. | Item Abbr. | Item Description |  |  | Calculation Procedure | Dimensions, IP | Numerical Input and Formulas
1 | 1 | COIL PHYSICAL DATA | 1 | Di | Tube Inside Diameter (See Form 410-1) |  |  |  | in
2 | 2 |  | 2 | Nt | Total Number of Tubes in Coil |  |  |  | --
3 | 3 |  | 3 | Nc | Number of Tube Circuits in Coil |  |  |  | --
4 | 4 |  | 4 | Aix | Total Cross-Sectional Fluid Flow Area |  |  | Aix = π/4*(Di/12)2*Nc | ft2 | 0
5 | 5 |  | 5 | Ls | Straight Tube Length per Pass |  |  |  | in
6 | 6 |  | 6 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  | in
7 | 7 |  | 7 | Le | Total Equivalent Length of Coil Circuit |  |  | = 1/12*[Ls*(Nt/Nc)+ Kb*(Nt/Nc-1)] | ft | 0
[10 empty] | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4
| 8 | LABORATORY TEST OBSERVATIONS AND CALCS OBTAINED FROM AHSRAE STANDARD 33-2000, FORMS 33TD-3 (water) or 33TD-4 (steam) | 8 | tw1 | Entering Water Temperature |  |  |  | °F
| 9 |  | 9 | tw2 | Leaving Water Temperature |  |  |  | °F
| 10 |  | 10 | twm | Mean Water Temperature |  |  |  | °F
8 |  |  | 11 | tvm | Mean Steam Temperature |  |  |  | °F
| 11 |  | 12 | ww | Water Flow Rate |  |  |  | lb/h
9 |  |  | 13 | wv | Steam Flow Rate |  |  |  | lb/h
10 |  |  | 14 | vvm | Average Saturated Steam Specific Volume |  |  |  | ft3/lb
| 12 |  | 15 | (hlw)T | Head Loss through Coil at Test Condition |  |  |  | ft H20
11 |  |  | 16 | ΔPv | Steam Pressure Drop in Coil |  |  |  | psi
| 13 | CALCULATION AND PLOTTING | 17 | Vw | Average Standard Water Velocity Inside Tubes |  |  | ww /(62.361*3600*Aix) | ft/s | 0 | 0 | 0 | 0
12 |  |  | 18 |  | Steam Flow Rate Inside Tubes |  |  | Will equal wv/Nc | lb/h | 0 | 0 | 0 | 0
| 14 |  | 19 | hhca | Header, Nozzles, and Tube Entrance and Exit Losses - to be established by manufacturer. hhca for Water Coils (hdr/conn assy) |  |  |  | ft H20
13 |  |  |  | ΔPh /vvm | ΔPh /vvmg for Steam Coils |  |  |  | lb2/ in2·ft3
| 15 |  | 21 | hLt/ (Le·Ft) | Water Pressure Drop Inside Tubes |  |  | hLt/(Le) = ((hlw)T - hhca)/(Le) | ft H20/ft tube lgth | 0 | 0 | 0 | 0
14 |  |  | 22 | ΔPtv/ (Le·Vvmg) | Pressure Drop Parameter for Steam Flow Inside Tubes |  |  | Eq. = (ΔPv/(Le*Vvmg)) - (ΔPh/Le) | lb2/ in2·ft3 | 0 | 0 | 0 | 0
| 16 |  | 23 |  | Plot hLt/LeFt vs. Vw on logarithmic coordinates. This curve with Fig 26 is used for applications for either hot or cold water coils |  |  |  | --
15 |  |  | 24 |  | Plot ΔPtv/LeVvmg vs. wv/Nc on logarithmic coordinates. This curve is used in obtaining steam coil application ratings. |  |  |  | --