## Form 410-6 IP Units
SUGGESTED FORM FOR RATING CALCULATION PROCEDURE FOR COOLING AND DEHUMIDIFYING COILS (Imperial Units, IP AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [9 empty] | Date
Solution Procedure Steps for Specific Coil Application |  |  |  | Coil Line: |  |  |  |  | Coil Type: |  | Choose Coil Type
|  |  |  | Coil Surface: | [6 empty] | Choose Calculation Method
|  |  |  | GENERAL PROCEDURE | [6 empty] | Choose Surface Condition
Cold Water Coils |  | Volatile Refrigerant Coils |  | General Procedure | Item No. | Item Abbr. | Item Description |  |  |  | Calculation Procedure | Dimensions, IP | Numerical Input and Formulas
Partially Wet Surface | Fully Wet Surface | Partially Wet Surface | Fully Wet Surface
1 | 1 | 1 | 1 | COIL PHYSICAL DATA | 1 | H | Coil Face Height |  |  |  |  | in
2 | 2 | 2 | 2 |  | 2 | L | Coil Face Length |  |  |  |  | in
3 | 3 | 3 | 3 |  | 3 | Af | Coil Face Area |  |  |  |  | ft2 | 0 | 0
4 | 4 | 4 | 4 |  | 4 | B | Surface Ratio (See Form 410-1) |  |  |  |  | --
5 | 5 | 5 | 5 |  | 5 | Nr | Coil Depth in Rows (Not known for "Solve for Rows" option) |  |  |  |  | --
6 | 6 | 6 | 6 |  | 6 | Ntr | Number of Tubes in each Coil Row |  |  |  |  | --
7 | 7 | 7 | 7 |  | 7 | Nc | Number of Tube Circuits in Coil |  |  |  |  | --
8 | 8 | 8 | 8 |  | 8 |  | Ao/(Af*Nr) |  |  |  |  | ft2/ftFA2-row
9 | 9 | 9 | 9 |  | 9 | Di | Tube Inside Diameter |  |  |  |  | in
10 | 10 | 10 | 10 |  | 10 | Ls | Straight Tube Length per Tube Pass |  |  |  |  | in
x | x |  |  |  | 11 | Ls/Di | Straight Tube Length per Pass/Tube Diameter |  |  |  |  | --
11 | 11 | 11 | 11 |  | 12 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  |  | in
12 | 12 | 12 | 12 | RATING CONDITIONS AND DATA COMPUTATIONS | 13 | Ao | Total External Coil Surface |  |  |  | Ao = (Ao/(Af*Nr))*Af*Nr | ft2 | 0 | 0
13 | 13 | 13 | 13 |  | 14 | Aix | Total Cross-Sectional Fluid Flow Area, Inside Tubes |  |  |  | Aix = π/4*(Di/12)2*Nc | ft2 | 0 | 0
14 | 14 | 14 | 14 |  | 15 | Le | Total Equivalent Length of Coil Circuit |  |  |  | Le = 1/12*((Nr*(Ls + Kb)*(Ntr/Nc)) - Kb) | ft | 0 | 0
15 | 15 | 15 | 15 |  | 16 | QaSTD | Air Volume Flow at Standard Conditions |  |  |  |  | scfm
16 | 16 | 16 | 16 |  | 17 | Va | Standard Air Face Velocity |  |  |  | Va = QaSTD/Af | std. ft/min | 0 | 0
17 | 17 | 17 | 17 |  | 18 | t1db | Entering Air Dry-Bulb Temperature |  |  |  |  | °F
18 | 18 | 18 | 18 |  | 19 | t1wb | Entering Air Wet-bulb Temperature |  |  |  |  | °F
19 | 19 | -- | -- |  | 20 | Vw | Avg. Standard Water Velocity |  |  |  |  | ft/s
20 | 20 | -- | -- |  | 21 | tw1 | Entering Water Temperature |  |  |  |  | °F
-- | -- | 19 | 19 |  | 22 | tr2g | Saturated Suction Refrigerant Temp at Coil Outlet (Note: For rating convenience, it is assumed that there is no temp drop from coil circuits to coil outlet trc2g = tr2g) |  |  |  |  | °F
-- | -- | 20 | 20 |  | 23 | tr2 | Superheated Refrigerant Temp at Coil Outlet (Note: For rating convenience, it is assumed that there is no temp drop from coil circuits to coil outlet (trc2g = tr2)) |  |  |  |  | °F
21 | 21 | 21 | 21 |  | 24 | Ps | Avg. Absolute Static Pressure at Coil |  |  |  |  | in Hg abs
-- | -- | 22 | 22 |  | 25 | tr0 | Liquid Refrigerant Temp Entering the Coil Control Device |  |  |  |  | °F
-- | -- | 23 | 23 |  | 26 | hr0 | Enthalpy of Refrigerant Entering Coil Control Device (From tro and Refrigerant Tables) |  |  |  |  | Btu/lb
22 | 22 | 24 | 24 |  | 27 | h1 | Entering Air Enthalpy (Using t1db, t1wb, and Ps ) |  |  |  |  | Btu/lb
23 | 23 | 25 | 25 |  | 28 | 60wa | Standard Air Flow Rate |  |  |  | 60wa = 4.50*QaSTD | lb/h | 0 | 0
24 | 24 | 26 | 26 |  | 29 |  | Case I - (Solve for Rows) If t2wb is known, determine h2 at t2wb saturated and Ps. Then calculate qt = 60wa(h1-h2)
[7 empty] | Case II - (Solve for Rows) If qt is known, determine h2 and then t2wb. h2 = h1-(qt/60wa) |  |  |  |  | --
Case III - (Solve for Capacity) If Nr is known, assume qt or t2wb, find h2 and then t2wb or qt, respectively.
25 | 25 | 27 | 27 |  | 30 | t2wb | Leaving Air Wet-Bulb Temperature |  |  |  |  | °F
26 | 26 | 28 | 28 |  | 31 | h2 | Leaving Air Enthalpy If qt is known, h2 = h1-(qt/60wa) |  |  |  |  | Btu/lb | 0 | 0
27 | 27 | 29 | 29 |  | 32 | qt | Total Heat Transfer Capacity of Coil (Enter numerical value if known. If not known, assume a numerical value for a trial and error solution.) |  |  |  | qt = 60wa*(h1-h2) | Btu/h
28 | 28 | -- | -- |  | 33 | ww | Water Flow Rate |  |  |  | ww = 62.361*3600(Aix*Vw) | lb/h | 0 | 0
29 | 29 | -- | -- |  | 34 | tw2 | Leaving Water Temperature |  |  |  | tw2 = tw1 + qt/ww | °F | 0 | 0
-- | -- | 30 | 30 |  | 35 | Pr2 | Absolute Pressure of Refrigerant at Coil Outlet (From refrigerant tables with tr2g) |  |  |  |  | psia
-- | -- | 31 | 31 |  | 36 | hr2 | Enthalpy of Saturated Refrigerant Vapor at Coil Outlet Pressure (From refrigerant tables with tr2g. Assumed saturation for rating convenience) |  |  |  |  | Btu/lb
-- | -- | 32 | 32 |  | 37 | vr2g | Specific Volume of Saturated Refrigerant Vapor at Coil Outlet Pressure (From refrigerant tables with tr2g. Assumed saturation for rating convenience) |  |  |  |  | ft3/lb
-- | -- | 33 | 33 |  | 38 | wr | Refrigerant Flow Rate |  |  |  | wr = qt/(hr2-hr0) | lb/h | 0 | 0
-- | -- | 34 | 34 |  | 39 | wr/Nc | Refrigerant Flow Rate per Tube Circuit |  |  |  | wr/Nc | lb/h | 0 | 0
-- | -- | 35 | 35 |  | 40 |  | Δprc/(Le*vr2g) - Refrigerant Pressure Drop Parameter (From Fig. 18 with wr/Nc) |  |  |  |  | lb2/ in2·ft4
-- | -- | 36 | 36 |  | 41 |  | Δprh/vr2g - Outlet Header Refrigerant Pressure Drop Parameter with wr |  |  |  |  | lb2/ in2·ft3
-- | -- | 37 | 37 |  | 42 | Pr1 | Abs. Pressure of Refrigerant at Coil Inlet |  |  |  | Pr1 =Pr2+(vr2g)(Le*(ΔPrc/( Le*vr2g))+ΔPrh/vr2g) | psia | 0 | 0
-- | -- | 38 | 38 |  | 43 | Prc2 | Abs. Pressure of Refrigerant Leaving Coil Circuits |  |  |  | Prc2 = Pr2+(vr2g*(ΔPrh/vr2g)) | psia | 0 | 0
-- | -- | 39 | 39 |  | 44 | trc2g | Saturated Refrigerant Temperature Leaving Coil Circuit (From Prc2 and refrigerant tables) |  |  |  |  | °F
-- | -- | 40 | 40 |  | 45 | tr1 | Refrigerant Temperature Entering Coil Circuits (From refrigerant charts or NIST data with Pr1 and hr0) |  |  |  |  | °F
-- | -- | 41 | 41 |  | 46 | qt/Nc | Refrigerant Loading Rate per Tube Circuit |  |  |  | qt/Nc | Btu/h | 0 | 0
30 | 30 | -- | -- |  | 47 | twm | Mean Water Temperature in Coil |  |  |  | twm = 0.5*(tw1+tw2) | °F | 0 | 0
31 | 31 | -- | -- |  | 48 | ρw | Density of Water at Mean Water Temp., twm |  |  |  |  | lb/ft3
32 | 32 | -- | -- |  | 49 | cpw | Specific Heat of Water at Mean Water Temp., twm |  |  |  |  | Btu/lb·°F
33 | 33 | -- | -- |  | 50 | μw | Dynamic Viscosity of Water at Mean Water Temp., twm |  |  |  |  | lb/ft·h
34 | 34 | -- | -- |  | 51 | kw | Thermal Conductivity of Water at Mean Water Temp., twm |  |  |  |  | Btu·ft/ h·ft2·°F
35 | 35 | -- | -- |  | 52 | Prw | Prandtl Number of Water at Mean Water Temp, twm |  |  |  | cpw*μw/kw | - | 0 | 0
36 | 36 | -- | -- |  | 53 | Prw2/3 |  |  |  |  | (cpw*μw/kw)2/3 | - | 0 | 0
37 | 37 | -- | -- |  | 54 | Gw | Mass Velocity of Water at Mean Water Temp., twm |  |  |  | ww/Aix | lb/h·ft2 | 0 | 0
38 | 38 | -- | -- |  | 55 | Rew | Reynolds Number of Water at Mean Water Temp., twm |  |  |  | Rew = Gw*Di/(12*μw) | - | 0 | 0
39 | 39 | -- | -- |  | 56 | jw | Colburn j Factor from Fig. 3 with Rew and Ls/Di |  |  |  |  | -
40 | 40 | -- | -- |  | 57 | (μtw/ μw).14 init | Estimate Dynamic Viscosity Ratio (VRinit) For air-cooling coils with water use initial estimate of 0.98
41 | 41 | -- | -- |  | 58 | fw | Estimate of Water Side Film Heat Transfer Coefficient |  |  |  | jw*cpw*Gw/(Prw2/3*μtw/μw0.14) | Btu/ h·ft2·°F | 0 | 0
42 | 42 |  |  |  | 59 | Rffa | Fouling Factor Allowance for Water (assumed to be zero unless otherwise specified) |  |  |  |  | h·ft2·°F /Btu
43 | 43 | -- | -- |  | 60 |  | Estimate of Tube Side Film Thermal Resistance: | [5 empty] | 0 | 0
44 | 44 |  |  |  |  | Rw | For Water Coils |  |  |  | = B(1/fw + Rffa) | h·ft2·°F /Btu | 0 | 0
|  | 42 | 42 |  |  | Rr | For Volatile Refrig Coils (Obtain Rr/B from Fig. 6 with qt/Nc) |  |  |  | Rr = (Rr/B) * B | h·ft2·°F /Btu
45 | 45 | 43 | 43 | RATING PARAMETERS | 61 | RaD | Air Film Thermal Resistance for Dry Surface (From Fig. 17 or 18 with Va) |  |  |  |  | h·ft2·°F /Btu
46 | 46 | 44 | 44 |  | 62 | RaW | Air Film Thermal Resistance for Wet Surface (From Fig. 17 or 18 with Va) |  |  |  |  | h·ft2·°F /Btu
47 | 47 | 45 | 45 |  | 63 | RmD | Metal Thermal Resistance for Dry Surface (From Fig. 14 with fa = 1/RaD) |  |  |  |  | h·ft2·°F /Btu
48 | 48 | 46 | 46 |  | 64 | C | Approximate Coil Characteristic *The approx value of C is used only to obtain the final value of RmW | [5 empty] | 0 | 0
[8 empty] | Cold Water |  |  | C = (Rw+RmD)/(0.243*RaW) | lb·°F /Btu | 0 | 0
[8 empty] | Volatile Refrigerant |  |  | C = (Rr+RmD)/(0.243*RaW) | lb·°F /Btu | 0 | 0
49 | 49 | 47 | 47 |  | 65 | y | Ratio of Tube-Side Temperature Difference to Air Enthalpy Difference |  |  |  |  | lb·°F /Btu | 0 | 0
[8 empty] | Cold Water |  |  | y = (tw2 - tw1)/(h1-h2) | lb·°F /Btu | 0 | 0
[8 empty] | Volatile Refrigerant |  |  | y = (tr1 - trc2g)/(h1-h2) | lb·°F /Btu | 0 | 0
50 | 50 | 48 | 48 |  | 66 | t1dp | Entering Air Dew Point Temperature Note: Calculation of Dew Point Temp for Non-Standard Air Pressure* |  |  |  | From Psychrometric Chart with Ps, t1db, and t1wb | °F
pv, IP = p'-[((ps-p')*(t1db-t1wb))/(2830-(1.44*t1wb))]
Where: ps = Air Pressure. p' = Sat. Vapor Press. at t1db from steam tables. Pv = Sat. Vapor Press. at Dew Point Temp.
Note: t1dp = Dew Point Temp. is Sat. Temp. Corresponding to Sat. Vapor Pressure, pv, from Steam Tables.
51 | 51 | 49 | 49 |  | 67 | h1dp | Enthalpy of Saturated Air at Dew Point Temp. (From psychrometric charts with t1dp and Ps) |  |  |  |  | Btu/lb
52 | 52 | 50 | 50 |  | 68 | hB | Approximate Air Enthalpy at Dry-Wet Boundary |  |  |  | hBcalc can't exceed h1 | Btu/lb | 0 | 0
[9 empty] | Selection of hBcalc |  | Selection of hBcalc from below | Btu/lb | 0 | 0
[9 empty] | Cold Water |  | (t1dp-tw2+(y*h1)+(C*h1dp))/(C+y) | Btu/lb | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | (t1dp-tr1+(y*h1)+(C*h1dp))/(C+y) | Btu/lb | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | (t1dp-trc2g - y*h1)+(C*h1dp))/(C - y) | Btu/lb | 0 | 0
53 | 53 | 51 | 51 |  | 69 | twB or trB | Approximate Tube-Side Fluid Temp at Dry-Wet Boundary |  |  |  |  | °F | 0 | 0
[9 empty] | Cold Water |  | twB = tw2-y*(h1 - hB) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | trB = tr1-y*(h1 - hB) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | trB = trc2g + y*(h1 - hB) | °F | 0 | 0
54 | 54 | 52 | 52 |  | 70 | twmW or trmW | Mean Tube-Side Fluid Temperature for Fully-Wet Coil or Wet Portion of Partially Dry Coil |  |  |  |  | °F | 0 | 0
[9 empty] | Cold Water |  | twmW=(tw1+tw2)/2 or =(twB+tw2)/2 | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | trmW=(tr1+trc2g)/2 or =(trB+trc2g)/2 | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | trmW=(tr1+trc2g)/2 or =(trB+tr1)/2 | °F | 0 | 0
55 | 55 | 53 | 53 |  | 71 | hmW | Approx. Mean Air Enthalpy for Fully-Wet Coil or Wet Portion of Partially Dry Coil |  |  |  | hmW=(h1+h2)/2 or =(hB+h1)/2 | Btu/lb | 0 | 0
56 | 56 | 54 | 54 |  | 72 | tsmW | Approx. Mean Surface Temp. for Fully Wet Coil or Wet Portion of Partially Dry Coil (With Items 64, 70, and 71) |  |  |  |  | °F
57 | 57 | 55 | 55 |  | 73 | m"/ cp | Air-Side Heat Transfer Multiplier for Wet Coil or Wet Portion of Partially Dry Coil (From Equation 44) |  |  |  |  | --
58 | 58 | 56 | 56 |  | 74 | faW | Air-Side Thermal Conductance for Wet Surface |  |  |  | faW = (m"/cp)/RaW | Btu/ h·ft2·°F | 0 | 0
59 | 59 | 57 | 57 |  | 75 | RmW | Metal Thermal Resistance for Wet Surface (From Fig. 14 with faW) |  |  |  |  | h·ft2·°F /Btu
60 | 60 | 58 | 58 |  | 76 | C | Coil Characteristics for Wetted Surface *The approx value of C is used only to obtain the final value of RmW |  |  |  | C = (Rw+RmW)/(0.243*RaW) or = (Rr+RmW)/(0.243*RaW) | lb·°F /Btu | 0 | 0
61 | 61 | 59 | 59 |  | 77 | hB | Air Enthalpy at Boundary |  |  |  | hBcalc can't exceed h1 | Btu/lb | 0 | 0
[9 empty] | Selection of hBcalc |  | Selection of hBcalc from below |  | 0 | 0
[9 empty] | Cold Water |  | hB = (t1dp-tw2+(y*h1)+(C*h1dp))/(C+y) | Btu/lb | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | hB = (t1dp-tr1+(y*h1)+(C*h1dp))/(C+y) | Btu/lb | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | hB = (t1dp-trc2g -(y*h1)+(C*h1dp))/(C-y) | Btu/lb | 0 | 0
62 | 62 | 60 | 60 |  |  | hm | Mean Air Enthalpy |  |  |  | = 0.5*(h1 + h2) | Btu/lb | 0 | 0
[5 empty] | 78 |  | For a Partially Dry Surface: If hm >= hB complete Items 79, 80, 83, etc. (Skip Items 81 and 82). If hm < hB complete Items 81,82, 83,etc. (Skip Items 79 and 80) For a Fully Wet Surface: Complete Items 81, 82, 83, etc. (Skip Items 79 and 80 ) |  |  |  |  | _
63 |  | 61 |  |  | 79 | tmdb | Air Dry-Bulb Temp where Tube-Side Fluid Temp Equals twm |  |  |  | = t1db - (0.5*qt)/(0.243*60wa) | °F | 0 | 0
64 |  | 62 |  |  | 80 | ttwm | Mean Tube Wall Temperature |  |  |  | = twm + (tmdb - ttwm)*(Rw)/(RaD+RmD+Rw) | °F | 0 | 0
65 | 63 |  |  |  | 81 | tsm | Surface Temp Where Tube-Side Fluid Temp Equals twm |  |  |  | From Fig 9 with Ps, twm, C and hm | °F
66 | 64 |  |  |  | 82 | ttwm | Mean Tube Wall Temperature |  |  |  | = twm+Rw*(tsm - twm)/(RmW + Rw) | °F | 0 | 0
67 | 65 | -- | -- |  | 83 | μtw | Dynamic Viscosity of Water at Tube Wall Temp., ttwm (Item 80 or 82) |  |  |  |  | lb/ft·h
68 | 66 | -- | -- |  | 84 | (μtw/ μw).14 calc | Calculated Dynamic Viscosity Ratio (VRcalc) If VRinit is not within 2 % of VRcalc , use VRcalc as new VRinit and recalculate starting at Item 57 Otherwise, procede to next Item | [5 empty] | 0 | 0
69 | -- | 64 | -- |  | 85 | qtD | Capacity for Dry Portion of Coil |  |  |  | qtD = 60wa*(h1-hB) | Btu/h | 0 | 0
70 | -- | 65 | 61 |  | 86 | tBdb | Air Dry-Bulb Temperature at Boundary |  |  |  | tB = t1db-(qtD/(0.243*60wa) | °F | 0 | 0
71 | -- | 66 | -- |  | 87 | twB or trB | Tube-Side Fluid Temperature at Boundary |  |  |  |  | °F | 0 | 0
[9 empty] | Cold Water |  | twB = tw2-y*(h1-hB) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | trB = tr1-y*(h1-hB) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | trB = trc2g + y*(h1-hB) | °F | 0 | 0
72 | -- | 67 | -- |  | 88 | Δtm | Logarithmic Mean Temperature Difference for Dry Coil Portion |  |  |  |  | -- | 0 | 0
[9 empty] | Cold Water |  | Δtm = ((t1db-tw2)-(tBdb-twB)) / (ln((t1db-tw2)/(tBdb-twB))) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Counterflow) |  | Δtm = ((t1db-tr1)-(tBdb-trB)) / (ln((t1db-tr1)/(tBdb-trB))) | °F | 0 | 0
[9 empty] | Volatile Refrigerant (Thermal Parallel Flow) |  | Δtm = ((t1db-trc2g)-(tBdb-trB)) / (ln((t1db-trc2g)/(tBdb-trB))) | °F | 0 | 0
73 | -- | 68 | -- |  | 89 | AcD | Calculated External Surface Area for Dry Portion of Coil |  |  |  | AcD = qtD*(RaD + Rw + RmD)/Δtm or AcD = qtD*(RaD + Rr + RmD)/Δtm | ft2 | 0 | 0
74 | 67 | 69 | 62 |  | 90 | qtW | Capacity for Wet Portion of Coil |  |  |  | qtW = qt-qtD or qtW = qt | Btu/h | 0 | 0
75 | 68 | 70 | 63 |  | 91 | ts1 or tsB | Surface Temperature at Air Entering Side of Wet Portion with: - Ps, h1, tw2, and C (Items 24,27,34, & 76) for Totally Wet Water Coils - Ps, h1, tr1, and C (Items 24,27,45 & 76) for Totally Wet Thermal Counterflow Volatile Refrigerant Coils - Ps, h1, trc2g, and C (Items 24,27,44, & 76) for Totally Wet Thermal Parallel Flow Volatile Refrigerant Coils Also, tsB = t1dp (Item 66) for Partially Dry Water and Refrigerant Coils |  |  |  |  | °F
76 | 69 | 71 | 64 |  | 92 | ts2 | Surface Temperature at Air Leaving Side of Wet Portion with: - Ps, h2, tw1, and C (Items 24,31,21 & 76) for Wet Water Coils - Ps, h2, trc2g, and C (Items 24,31,44 & 76) for Wet Thermal Counterflow Volatile Refrig Coils - Ps, h2, tr1, and C (Items 24,31,45 & 76) for Wet Thermal Parallel Flow Volatile Refrig Coils |  |  |  |  | °F
77 | 70 | 72 | 65 |  | 93 | hs1 | Enthalpy of Saturated Air at Air Entering Side of Wet Portion. - From Ps, and ts1 - For Fully-Wet Coils hsB = h1dp (Item 67) for Partially Dry Coils |  |  |  |  | Btu/lb
78 | 71 | 73 | 66 |  | 94 | hs2 | Enthalpy of Saturated Air at Ps and ts2 |  |  |  |  | Btu/lb
79 | 72 | 74 | 67 |  | 95 | Δhm | Logarithmic Mean Enthalpy Difference Between Air Stream and Wetted Surface |  |  |  |  | Btu/lb | 0 | 0
[9 empty] | Fully Wet Surface |  | Δhm=((h1-hs1)-(h2-hs2)) / (ln((h1-hs1)/(h2-hs2)) | Btu/lb | 0 | 0
[9 empty] | Partially Wet Surface |  | Δhm=((hB-hsB)-(h2-hs2)) / (ln((hB-hsB)/(h2-hs2)) | Btu/lb | 0 | 0
80 | 73 | 75 | 68 |  | 96 | AcW | Calculated External Surface Area for Fully Wet Coil or Wet Portion of Coil |  |  |  | AcW = 0.243*RaW*qtW/Δhm | ft2 | 0 | 0
81 | 74 | 76 | 69 |  | 97 | Ac | Total Calculated External Surface Area Note: For Case I and II in Item 29, skip Items 100 and 101. For Case III in Item 29, skip Items 98 and 99. |  |  |  |  | ft2 | 0 | 0
82 | 75 | 77 | 70 |  | 98 | Nr | Calculated Number of Coil Rows Required |  |  |  | Nr = Ac/(Af*(Ao/(Af*Nr))) | -- | 0 | 0
83* | 76* | 78* | 71* |  | 99 | Nr | Coil Row Depth Installed for "Solve for Rows" option |  |  |  |  | --
84 | 77 | 79 | 72 | CALC OF CAPACITY FOR CASE III | 100 |  | If Ac > or < Ao, assume a new value of qt that's < or > Item 32. Repeat calculations from Item 29 through Item 97. Plot calculated values of Ac against assumed values of Item 32 as shown in Fig. F410-6.1 |  |  |  |  | --
85 | 78 | 80 | 73 |  | 101 | qt | Determine the actual value of qt from plot in Item 100 and enter value (From Fig F410-6.1 with Ac = Ao ) |  |  |  |  | Btu/h
86 | 79 | 81 | 74 | CALCULATIONS TO DETERMINE AIR LEAVING DRY-BULB TEMPERATURE AND SENSIBLE CAPACITY | 102 | c | Heat Transfer Exponent |  |  |  | c = Ao/(.243*RaD*(60wa)) |  | 0 | 0
87 | 80 | 82 | 75 |  | 103 | e-c | Heat Transfer Factor |  |  |  | e-c |  | 0 | 0
88 | 81 | 83 | 76 |  | 104 | h2 | Leaving Air Enthalpy at Actual Value of qt |  |  |  | h2 = h1-([qt (Item 32 or 101)]/60wa) | Btu/lb | 0 | 0
89 | 82 | 84 | 77 |  | 105 | hs̅ | Saturated Enthalpy at Effective Surface Temperature |  |  |  | hs̅ = h1 - (h1-h2)/ (1.0-e-c) | Btu/lb | 0 | 0
90 | 83 | 85 | 78 |  | 106 | ts̅ | Effective Surface Temperature from Psychrometric Chart with Ps and hs̅ |  |  |  |  | °F
91 | 84 | 86 | 79 |  | 107 | t2db | Air Leaving Dry-Bulb Temperature |  |  |  | t2db = ts̅ + (t1db - ts̅)*e-c | °F | 0 | 0
92 | 85 | 87 |  |  | 108 | qs | Sensible Heat Transfer Capacity of Coil |  |  |  | qs = .243*(60wa)*(t1db - t2db) | Btu/h | 0 | 0
93 | 86 | 88 |  |  | 109 | qs/qt | Sensible Heat Ratio |  |  |  |  | _ | 0 | 0
94 | 87 | 89 | 80 | AIR-SIDE FRICTION CALCULATIONS | 110 | ΔpsW/Nr | Air-Side Friction per Row Deep at Standard Conditions (Use wet surface for partially dry and fully wet coils) - From Fig. 17 with Va for Water Coils - From Fig. 18 with Va for Volatile Refrigerant Coils |  |  |  |  | in H20 /row
95 | 88 | 90 | 81 |  | 111 | Fa | Dry Surface Air-Side Pressure Drop Correction Factor |  |  |  | Fa = (460+0.5*(t1db+t2db))/ (17.71*Ps) | -- | 0 | 0
96 | 89 | 91 | 82 |  | 112 | (Δpa) JOB | Air-Side Friction at JOB Conditions (constant wa) |  |  |  | (ΔPa)JOB= (ΔpsW/Nr)*Fa*Nr | in H20 | 0 | 0
97 | 90 | -- | -- | TUBE SIDE PRESSURE DROP CALCULATIONS | 113 |  | Δpt/LeFt - Tube Circuit Water Pressure Drop Parameter at 60°F Mean Water Temp (From Fig. 16 with Vw) |  |  |  |  | ft H20 /ft
98 | 91 | -- | -- |  | 114 | hLhca/ Fh | Header, Nozzle, and Tube Entrance and Exit Losses to be Established by Manufacturer |  |  |  |  | ft H20
99 | 92 | -- | -- |  | 117 | (Δpw) JOB | Water Pressure Drop Across Coil at Job Conditions |  |  |  | (Δpw)JOB = (hLhca*Fh) + (Le*(Δpt/LeFt)*Ft) | ft H20 | 0 | 0
-- | -- | 92 | 83 |  | 118 | Δpr | Refrigerant Pressure Drop Through Coil |  |  |  | Δpr = (vr2g*(Δprc/(Le*vr2g)*Le +Δprh/vr2g ) | psi | 0 | 0
* If Solving for Rows and Item 5 is unknown
Figure F410-6.1