## Form 410-8 IP Units
SUGGESTED FORM FOR RATING CALCULATION PROCEDURE FOR SENSIBLE HEAT AIR COILS WITH ETHYLENE GLYCOL SOLUTIONS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [6 empty] | Date
Solution Procedure Steps for Specific Coil Application |  | Coil Line: |  |  |  | Coil Type: |  |  |  | Numerical Input and Formulas
Coil Surface:
GENERAL PROCEDURE
To Solve For Rows Deep (Nr) | To Solve For Capacity (qs) | General Procedure | Item No. | Item Abbr. | Item Description |  |  | Calculation Procedure | Dimensions, IP
-- | -- |  | -- | cp | Specific Heat at Constant Pressure |  |  |  | --
1 | 1 | COIL PHYSICAL DATA | 1 | H | Coil Face Height |  |  |  | in.
2 | 2 |  | 2 | L | Coil Face Length |  |  |  | in.
3 | 3 |  | 3 | Af | Coil Face Area |  |  |  | ft2
4 | 4 |  | 4 | B | Surface Ratio (See Form 410-1) |  |  |  | --
-- | 5 |  | 5 | Nr | Coil Depth in Rows |  |  |  | --
-- | 6 |  | 6 | Nt | Total Number of Tubes in Coil |  |  |  | --
5 | 7 |  | 7 | Nc | Number of Tube Circuits in Coil |  |  |  | --
6 | 8 |  | 8 |  | Ao/Af*Nr |  |  |  | ft2/ ft2-F.A.
-- | 9 |  | 9 | Ao | Total External Coil Surface |  |  | Ao = [8]*Af*Nr | ft.2 | 0
7 | 10 |  | 10 | Di | Tube Inside Diameter |  |  |  | in.
8 | 11 |  | 11 | Aix | Total Cross-Sectional Fluid Flow Area, Inside Tubes |  |  | Aix, IP = 0.00545*Di2*Nc | ft.2 | 0
9 | 12 |  | 12 | Ls | Straight Tube Length per Tube Pass |  |  |  | in.
10 | 13 |  | 13 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  | in.
11 | 14 |  | 14 | Ls /Di | Ratio of Tube Length to Diameter |  |  | Ls /Di | -- | #DIV/0!
12 | 15 | RATING CONDITIONS | 15 | Qa | Air Volume Flow at Standard Conditions |  |  |  | scfm
13 | 16 |  | 16 | Va | Standard Air Face Velocity |  |  | Va, IP = Qa/Af | ft/min | #DIV/0!
14 | 17 |  | 17 | t1 | Entering Air Dry-Bulb Temperature |  |  |  | °F
15 | 18 |  | 18 | tg1 | Entering Ethylene Glycol Temperature |  |  |  | °F
16 | 19 |  | 19 | Δt0 | Initial Air-to-Ethylene Glycol Solution |  |  | Select one of the following | °F | 0
[6 empty] | For Air-Cooling Coils |  | t1 - tg1 | °F | 0
[6 empty] | For Air-Heating Coils |  | tg1 - t1 | °F | 0
17 | 20 |  | 20 | Ps | Avg. Absolute Static Pressure at Coil |  |  |  | in. Hg abs
18 | 21 |  | 21 | wg | Total Ethylene Glycol Solution Flow Rate |  |  |  | lb per hr
19 | 22 |  | 22 | wg /Nc | Ethylene Glycol Solution Flow Rate per Circuit |  |  | wg/Nc | lb / hr circuit | #DIV/0!
20 | -- |  | 23 | qs | Coil Sensible Heat |  |  |  | Btuh
21 | -- |  | 24 | Δta | Air Temperature Rise or Drop Across Coil |  |  | Δta, IP = qs/(4.5*cp*Qa) | °F | #DIV/0!
22 | -- |  | 25 | t2 | Leaving Air Temperature at Coil
[6 empty] | For Air-Cooling Coils: |  | t2 = t1 - Δta | °F | #DIV/0!
[6 empty] | For Air-Heating Coils |  | t2 = t1 + Δta | °F | #DIV/0!
23 | 23 |  | 26 |  | Ethylene Glycol Concentration |  |  |  | % by wt
24 | 24 | ETHYLENE GLYCOL SOLUTION PROPERTIES AND CALCULATIONS | 27 | tgm | Mean Ethylene Glycol Solution Temperature - When solving for rows deep this value must be calculated by trial and error using [26] and determining cpg for various values of tgm with the following equations:
[6 empty] | For Air-Cooling Coils: |  | tgm = tg1 + qs/(2*wg*cpg) | °F | #DIV/0!
[6 empty] | For Air-Heating Coils |  | tgm = tg1 - qs/(2*wg*cpg) | °F | #DIV/0!
- When solving for capacity, this value must be approximated (suggest tgm be 5°F (2.8°C) to 10°F (5.6°C) from tg1)
25 | 25 |  | 28 | cpg | Specific Heat of Ethylene Glycol Solution at [26] & tgm |  |  |  | Btu /lb*°F
26 | 26 |  | 29 | dg | Specific Gravity of Ethylene Glycol Solution at [26] & tgm |  |  |  | --
27 | 27 |  | 30 | kg | Thermal Conductivity of Ethylene Glycol Solution at [26] & tgm |  |  |  | Btu/ hr *ft*°F
28 | 28 |  | 31 | μg | Absolute Viscosity of Ethylene Glycol Solution at [26] and tgm (Solution at [26] & [27] = centipoises x 2.42) |  |  |  | lb/ ft*hr
29 | 29 |  | 32 | νg | Kinematic Viscosity of Ethylene Glycol Solution |  |  | νg, IP = μg/(224500*dg) | ft.2/s | #DIV/0!
30 | 30 |  | 33 | Cg | Mass Velocity of Glycol |  |  | Cg = wg/Aix | lb /ft.2*hr | #DIV/0!
31 | 31 |  | 34 | Vg | Ethylene Glycol Solution Velocity Inside Tubes |  |  | Vg, IP = Cg/(224500*dg) | ft./s | #DIV/0!
32 | 32 |  | 35 | Re | Reynolds Number for Ethylene Glycol Solution |  |  | Re, IP = (Vg*Di)/(12*νg) | -- | #DIV/0!
33 | 33 |  | 36 | Pr | Prandtl Number for Ethylene Glycol Solution |  |  | Pr = cpg*μg/kg | -- | #DIV/0!
34 | 34 |  | 37 | Pr(2/3) |  |  |  | Pr(2/3) | -- | #DIV/0!
35 | 35 |  | 38 | j | Colburn Heat Transfer Factor for Ethylene Glycol Solution at Re, [14] and Fig. 3 |  |  |  | --
36 | 36 | GENERAL CALCULATIONS | 39 | RaD+ RmD | Combined Air Film plus Metal Thermal Resistance (From Fig. 16 with Va) |  |  |  | hr*ft2*F /Btu
37 | 37 |  | 40 | M | Air-to-Ethylene Glycol Solution Heat Capacity Ratio |  |  | M, IP = 4.5*Qa*cp/(wg*cpg) | -- | #DIV/0!
38 | -- |  | 41 | E | Air-Side Effectiveness |  |  | E = Δta / Δt0
[6 empty] | For Air-Cooling Coils |  |  | -- | #DIV/0!
[6 empty] | For Air-Heating Coils |  |  | -- | #DIV/0!
39 | -- |  | 42 | Co | Heat Transfer Exponent (Air-to-Ethylene Glycol Solution) '-From Section 6.5 |  |  |  | --
40 | -- |  | 43 | Δtm | Overall Mean Temperature Difference |  |  | Δtm = Δta / Co | °F | #DIV/0!
41 | 38 |  | 44 | ttw | Average Tube Wall Temperature -When solving for rows deep this temperature must be approximated, suggest:
[6 empty] | For Air-Cooling Coils |  | ttw = tgm + 0.5*Δtm | °F | #DIV/0!
[6 empty] | For Air-Heating Coils |  | ttw = tgm - 0.5*Δtm | °F | #DIV/0!
- When solving for capacity, this value must be approximated (suggest ttw be 10°F (5.6°C) to 15°F (8.3°C) from tg1)
42 | 39 |  | 45 | μtw | Absolute Viscosity of Ethylene Glycol Solution at [26] and ttw |  |  |  | lb /ft.*hr
43 | 40 |  | 46 | (μtw/ μg)0.14 | Viscosity Ratio |  |  | (μtw/ μg)0.14 | -- | #DIV/0!
44 | 41 |  | 47 | fg | Ethylene Glycol Solution Film Heat Transfer Coefficient |  |  | fg = (cpg*Cg*j)/((Pr(2/3))*[46]) | Btu/ hr *ft2*°F | #DIV/0!
45 | 42 |  | 48 | Rg | Film Thermal Resistance of Ethylene Glycol Solution |  |  | Rg = B/fg | hr*ft2*F /Btu | #DIV/0!
46 | 43 |  | 49 | R |  |  |  |  | hr*ft2*F /Btu
47 | -- | CALCULATIONS TO SOLVE FOR ROWS DEEP | 50 | *ttw | Average Tube Wall Temperature
[6 empty] | For Air-Cooling Coils |  | *ttw=tgm + (Rg/R)*Δtm | °F | #DIV/0!
[6 empty] | For Sir-Heating Coils |  | *ttw=tgm - (Rg/R)*Δtm | °F | #DIV/0!
*Must equal [44] with +/- 3°F (+/-1.7°C). If not, assume a new value for [44] and repeat calculations through *ttw
48 | -- |  | 51 | Nrc | Calculated Row Depth Required |  |  | Nrc= (qs*R*Co)/(Af*[8]*Δta) | -- | #DIV/0!
49 | -- |  | 52 | Nr | Integral Coil Row Depth Installed |  |  |  | --
50 | -- |  | 53 | Nt | Total Number of Tubes in Coil |  |  |  | --
-- | 44 | CALCULATIONS TO SOLVE FOR CAPCITY | 54 | Co | Heat Transfer Exponent (Air-to-Ethylene Glycol Solution) |  |  | Co, IP = Ao/(4.5*cp*Qa*R) | -- | #DIV/0!
-- | 45 |  | 55 | E | Air-Side Effectiveness (From Section 6.5) |  |  |  | --
-- | 46 |  | 56 | Δta | Air Temperature Rise or Drop Across Coil |  |  | Δta = E*Δto | °F | 0
-- | 47 |  | 57 | Δtg | Ethylene Glycol Solution Temperature Rise or Drop Across Coil |  |  | Δtg = [56]*M | °F | #DIV/0!
-- | 48 |  | 58 | Δtm | Overall Mean Temperature Difference |  |  | Δtg = [56]/[54] | °F | #DIV/0!
-- | 49 |  | 59 | *tgm | Mean Ethylene Glycol Solution Temperature
[6 empty] | For Air-Cooling Coils |  | tgm = tg1 + 0.5*[57] | °F | #DIV/0!
[6 empty] | For Air-Heating Coils |  | tgm = tg1 - 0.5*[57] | °F | #DIV/0!
-*tgm must equal [27] and [60] must equal [44] with +/- 3°F (+/-1.7°C). If not, assume new values for [27] and [44] and repeat calculations through *tgm
-- | 50 |  | 60 | *tgm | Average Tube Wall Temperature
[6 empty] | For Air-Cooling Coils |  | *tgm=[59]+([48]/[49])*[58] | °F | #DIV/0!
[6 empty] | For Air-Heating Coils |  | *tgm=[59]-([48]/[49])*[58] | °F | #DIV/0!
-*tgm must equal [27] and [60] must equal [44] with +/- 3°F (+/-1.7°C). If not, assume new values for [27] and [44] and repeat calculations through *tgm
-- | 51 |  | 61 | qs | Coil Sensible Heat |  |  | qs, IP = (4.5*cp*Qa*[56]) | Btuh | 0
-- | 52 |  | 62 | t2 | Leaving Air Temperature at Coil |  |  | Select one of the following |  | 0
[6 empty] | For Air-Cooling Coils |  | t2 = t1 - [56] | °F | 0
[6 empty] | For Air-Heating Coils |  | t2 = t1 + [56] | °F | 0
51 | 53 | GENERAL CALCULATIONS | 63 | Δpst /Nr | Air-Side Friction per Row Deep at Standard Conditions (From Fig. 15 or 16 with Va) |  |  |  | in. H20 /row
52 | 54 |  | 64 | Fa | Air-Side Pressure Drop Correction Factor |  |  | Fa, IP = (460+((t1+[25] or [62])/2)) /(17.71*Ps) | -- | #DIV/0!
53 | 55 |  | 65 | (ΔPa) JOB | Air-Side Friction at JOB Conditions (constant wa) |  |  | (ΔPw)JOB=([63]*[64])*([5] or [52]) | in. H20 | #DIV/0!
54 | 56 |  | 66 | Le | Total Equivalent Length of Coil Circuit |  |  | Le, IP=0.0833*[Ls*([6] or [53]/ Nc)+Kb*(([6] or [53]/Nc)-1)] | ft. | #DIV/0!
55 | 57 |  | 67 | f' | Friction Factor for Ethylene Glycol Solution (From Fig. 3 at Re) |  |  |  | --
56 | 58 |  | 68 | Δpt /Le | Ethylene Glycol Solution Pressure Drop Inside Tubes |  |  | (f'*Vg2*[46])/(1.34*Di) | ft. of Glycol per ft tube | #DIV/0!
57 | 59 |  | 69 | Δph | Header and Tube Entrance and Exit Loss -Established by the manufacturer |  |  |  | ft. of Glycol
58 | 60 |  | 70 | (ΔPg) JOB | Ethylene Glycol Solution Pressure Drop Across Coil at Job Conditions |  |  | (ΔPg)JOB = ([66]*[68]) + [69] | ft. of Glycol | #DIV/0!